## Sayfa1
Fill |  | cells
General |  |  | Core (square)
vin (volt) | 3000 |  | required core area(m^2) | 0.067568
Nprimary(turn) | 20 |  | real core area (m^2) | 0.075075 |  | Leakage Inductance
B(tesla) | 1 |  | core depth(m) | 0.274 |  | Permability | 0.0016125 | mr | 1283.8376
f(hz) | 500 |  |  |  |  | L path (m) | 2.126
Nsecondary turn | 2000 |  |  |  |  | operating H(A/m) | 620
|  |  | Stacking factor | 0.9 |  | H*L | 1318.12
primary cable dimensions (mm) AxB | 27 | 27 | Core loss at 1 teslaW/kg | 7.5 |  | Area (m^2) | 0.067568
secondary cable dimensions (mm) AxB | 2.9 | 2.9 | loss coefficient W/kg | 7.5 |  | Reluctance | 19513.0543
Insulation per layer hV (mm) | 1.5 |  |  |  |  | Magnetizing flux | 0.067551
Insulation per layer LV (mm) | 0.5 |  |  |  |  | current | 2200
[6 empty] | turns | 20
Windings | [5 empty] | Inductance | 0.0006141
Primary turns per layer | 10 |  |  |  |  | X(j*ohm) | 1.9283
Secondary turns per layer | 80 |  | gap height(mm) | 300
primary layers | 2 |  | gap lenght(mm) | 250 |  |  | 0.020499
secondary layers | 25 |  | Core height(mm) | 847.9966
Hprimary winding (mm) | 270 |  | Core lenght(mm) | 797.9966
Hsecondary winding(mm) | 232 |  | Core volume(cm^3) | 148377.9222 |  | Circuit Reluctance
Lprimary(mm) | 55 |  | Core density (gr/cm^3) | 7.5 |  | L path (m) | 2.196
Lsecondary(mm) | 110 |  | Core weight (kg) | 1112.8344 |  | Area(m^2) | 0.067568
[6 empty] | Permability | 0.0016125
[6 empty] | Reluctance | 20155.4729
Windings are assumed square |  |  | Core Loss kW | 8.3463 |  | Mag ind (Henry) | 0.019846
|  |  | Copper Loss kW | 8.8725 | at full load | Mag reactance | 62.3156
L1avg primary winding (mm) | 301.4983 |  |  |  |  | Mag current | 48.1421
L1avg secondary winding (mm) | 328.9983 |  | Total Loss kW | 17.2187
L primary (m) | 26.1199 |  | Efficiency | 0.99736
Lsecondary (m) | 2633.9865
Resistivity heat coefficient | 1.3 |  | Skin Depth Calculation
R per meter primary ohm/m | 3.4944e-05 |  | resistivity at 110 C | 2.184e-08
R per metersecondary ohm/m | 0.0034944 |  | angular frequency | 3140
Rprimary | 0.00091273 |  | permeability | 1.257e-06
Rsecondary | 9.2042 |  | skin depth(mm) | 3.3267
Loss primary | 4417.6256
Loss secondary | 4454.834